## CT Data Entry Table
Current (Amperage) Calculation | User Input |  | Calculated Value | Wire Size (inches) Calculation | User Input |  | Calculated Area Of Conductors
#1 |  |  |  | How Many Conductors Per Phase Are Specified | 2
Power (kW) Rating Of Inverter Type #1 |  | 0 |  | Select The Specified Wire Size (MCM / kCMIL / AWG) | 4/0' | 0.7 | 0.7693
# Of Inverters Of Inverter Type #1 |  |  |  | OR
Voltage (VAC) / Phase Rating Of Inverter Type #1 |  | #N/A | 0 | Total Wire Size Area (0-13.75 Sq. Inches) |  |  | 0
Power (kW) Rating Of Inverter Type #2 |  | 0 |  | Enter "Yes" if you would like to utilize this method for Calculating Wire Size. See Note For More Information. | No | 0
# Of Inverters Of Inverter Type #2 |  |  |  | Current (Amperage) Used To Calculated Wire Size | 300 | 0.84 | 0
Voltage (VAC) / Phase Rating Of Inverter Type #2 |  | #N/A | 0 | Wire Size As Calculated From Current (Amps) | 300 MCM / kCMIL
Power (kW) Rating Of Inverter Type #3 |  | 0
# Of Inverters Of Inverter Type #3
Voltage (VAC) / Phase Rating Of Inverter Type #3 |  | #N/A | 0
Total Inverter Amperage |  |  | 0
#2
Maximum Current (0-2400 Amps) To Be Monitored | 300 |  | 300
Percent Match - #1 vs #2 |  |  | 0%
#3
Enter Overload Protection |  |  | 0
Current (Amperage) To Be Monitored |  |  | 300 | Maximum Wire Size |  |  | 0.7693
Customer Sign Off - Current To Be Monitored: |  |  |  | Customer Sign Off - Wire Size To Be Monitored:
Note on G9: Brian: The following section is the wire area calculated based on system current (Amps). This is not the ideal method for entering the wire size. If possible utilize the wire size and conductor quantity above first. If you choose to utilize this method because wire size cannot be found select "Yes" in the adjacent cell.
Note on B18: Enter the total current to be monitored. This is the sum of the output of each inverter being monitored with one meter. The Photon Website Database will tell you the current (Amperage) output of specific inverters. This value will only be used secondarily if the above information is not entered.
Note on B21: The Overload Protection value should only be used as a last resort when sizing CT’s. Only use the Overload protection value when #1 & #2 above cannot be determined.

## CT Acceptable Part # Report
First Preference | Manufacturer | Model | Reason For Selecting This Model | Acceptable CT Based On Information Provided | Part Number | % Match For Current Range Greater Then 75% Indicates Current Measured Is Ok, Less Than 74% Indicates Current Is To Low To Measure | % Match For Window Size Greater Then 91% Indicates Wire Is Too Large, Less Then 90% Indicates Wire Is Ok | Acceptable CT Based On Specified Wire Size & | Select CT To Be Supplied
| Continental Control System | CTS-1250 | Accuracy ±1% from 10% to 100% of rated current, 0-600VAC, 1.25"x1.25" Window | TRUE | CTS-1250-300 | 100% | 54.71% | TRUE | No
| Continental Control System | CTS-2000 | Accuracy ±1% from 10% to 100% of rated current, 0-600VAC, 2.0"x2.0" Window | TRUE | CTS-2000-400 | 75% | 21.37% | FALSE | No
| Continental Control System | ACCU-CTs | Accuracy ±0.75% from 1% to 120% of rated primary current, 0-600VAC, .75"x.75" Window | FALSE | FALSE | 0% | 0% | FALSE | No
| Continental Control System | High Accuracy CT’s | Accuracy ±0.60% from 1% to 120% of rated primary current, 0-600VAC, .75"x.75" Window | FALSE | FALSE | 0% | 0% | FALSE | No
Second Preference
| Veris Industries | H681x | Accuracy ±0.50% from 5% to 120% of rated primary current, 0-600VAC, Window Size Varies | TRUE | H6810-300A-.3V | 100% | 54.79% | TRUE | No
| Elkor Technologies | MSCTx | Accuracy 1%, phase shift < 2 degrees, 0-600VAC, Window Size Varies | TRUE | MSCT2 | 50% | 54.71% | FALSE | No
Customer Sign Off - Current To Be Monitored By Meter:

## CT Selection Calculation (hidden)
Enter Maximum Current (0-2400 Amps) To Be Monitored | 300 | Enter Total Wire Size Area (0-13.75 Inches) | 0.7693
Veris CT's
Actual CT Current (Amps) Maximum Range | 300 | Actual CT Window Area (Inches) | 1.404
Appropriate CT Model Number Based On Current (Amps) | H6810
Appropriate CT Model Number Based On Wire Size | H6810
Is There An Acceptable Veris CT Based On Current & Wire Size | TRUE
Acceptable Veris CT Part Number | H6810-300A-.3V
Elkor CT's
Actual CT Current (Amps) Maximum Range | 600 | Actual CT Window Area (Inches) | 1.4062
Appropriate CT Model Number Based On Current (Amps) | MSCT2
Appropriate CT Model Number Based On Wire Size | MSCT2
Is There An Acceptable Elkor CT Based On Current & Wire Size | TRUE
Acceptable Elkor CT Part Number | MSCT2
Continental Control Systems Option #1
Actual CT Current (Amps) Maximum Range | 400 | Actual CT Window Area (Inches) | 3.6
Appropriate CT Model Number Based On Current (Amps) | CTS-2000
Appropriate CT Model Number Based On Wire Size | CTS-2000
Is There An Acceptable Continental Control Systems CT Based On Current & Wire Size | TRUE
Acceptable Continental Control Systems CT Part Number | CTS-2000-400
Continental Control Systems Option #2
Actual CT Current (Amps) Maximum Range | 300 | Actual CT Window Area (Inches) | 1.4062
Appropriate CT Model Number Based On Current (Amps) | CTS-1250
Appropriate CT Model Number Based On Wire Size | CTS-1250
Is There An Acceptable Continental Control Systems CT Based On Current & Wire Size | TRUE
Acceptable Continental Control Systems CT Part Number | CTS-1250-300
Continental Control Systems Option #3
Actual CT Current (Amps) Maximum Range | #N/A | Actual CT Window Area (Inches) | #N/A
Appropriate CT Model Number Based On Current (Amps) | #N/A
Appropriate CT Model Number Based On Wire Size | #N/A
Is There An Acceptable Continental Control Systems CT Based On Current & Wire Size | #N/A
Acceptable Continental Control Systems CT Part Number | #N/A
Continental Control Systems Option #4 (High Accuracy CT's .6%)
Actual CT Current (Amps) Maximum Range | #N/A | Actual CT Window Area (Inches) | #N/A
Appropriate CT Model Number Based On Current (Amps) | #N/A
Appropriate CT Model Number Based On Wire Size | #N/A
Is There An Acceptable Continental Control Systems CT Based On Current & Wire Size | #N/A
Acceptable Continental Control Systems CT Part Number | #N/A

## CT Sizing Table - Veris (hidden)
http://www.mrexcel.com/articles/excel-vlookup-index-match.php | Model Number | Maximum Current | Maximum Wire Size (Inches) | Maximum Wire Area (sq. in.) | Meter Voltage Input
H6812-2400A-.3V | H6812 | 2400 | 5.5” x 2.5” | 12.375 | .3V
H6812-2000A-.3V | H6812 | 2000 | 5.5” x 2.5” | 12.375 | .3V
H6812-1600A-.3V | H6812 | 1600 | 5.5” x 2.5” | 12.375 | .3V
H6812-1200A-.3V | H6812 | 1200 | 5.5” x 2.5” | 12.375 | .3V
H6812-1000A-.3V | H6812 | 1000 | 5.5” x 2.5” | 12.375 | .3V
H6811-800A-.3V | H6811 | 800 | 2.9” x 2.5” | 6.525 | .3V
H6811-600A-.3V | H6811 | 600 | 2.9” x 2.5” | 6.525 | .3V
H6811-400A-.3V | H6811 | 400 | 2.9” x 2.5” | 6.525 | .3V
H6810-300A-.3V | H6810 | 300 | 1.2” x 1.3” | 1.404 | .3V
H6810-200A-.3V | H6810 | 200 | 1.2” x 1.3” | 1.404 | .3V
H6810-100A-.3V | H6810 | 100 | 1.2” x 1.3” | 1.404 | .3V

## CT Sizing Table - Elkor (hidden)
http://www.mrexcel.com/articles/excel-vlookup-index-match.php | Maximum Current | Maximum Wire Size (Inches) | Maximum Wire Area (sq. in.) | Meter Voltage Input
MSCT5 | 2000 | 3” x 5” | 13.5 | .3V
MSCT3 | 1000 | 2” x 2” | 3.6 | .3V
MSCT2 | 600 | 1.25” x 1.25” | 1.4062 | .3V
MSCT1 | 200 | .75” x .75” | 0.50625 | .3V

## CT Sizing Table - CCS (hidden)
http://www.mrexcel.com/articles/excel-vlookup-index-match.php | Model Number | Maximum Current | Maximum Wire Size (Inches) | Maximum Wire Area (sq. in.) | Meter Voltage Input
CTS-2000-1500 | CTS-2000 | 1200 | 2" x 2" | 3.6 | .3V
CTS-2000-1200 | CTS-2000 | 1200 | 2" x 2" | 3.6 | .3V
CTS-2000-1000 | CTS-2000 | 1000 | 2" x 2" | 3.6 | .3V
CTS-2000-800 | CTS-2000 | 800 | 2" x 2" | 3.6 | .3V
CTS-2000-600 | CTS-2000 | 600 | 2" x 2" | 3.6 | .3V
CTS-2000-400 | CTS-2000 | 400 | 2" x 2" | 3.6 | .3V
CTS-1250-600 | CTS-1250 | 600 | 1.25" x 1.25" | 1.4062 | .3V
CTS-1250-400 | CTS-1250 | 400 | 1.25" x 1.25" | 1.4062 | .3V
CTS-1250-300 | CTS-1250 | 300 | 1.25" x 1.25" | 1.4062 | .3V
ACT-0750-250 | ACT-0750 | 250 | .75” x .75” | 0.50625 | .3V
ACT-0750-200 | ACT-0750 | 200 | .75” x .75” | 0.50625 | .3V
ACT-0750-100 | ACT-0750 | 100 | .75” x .75” | 0.50625 | .3V
ACT-0750-050 | ACT-0750 | 50 | .75” x .75” | 0.50625 | .3V
ACT-0750-030 | ACT-0750 | 50 | .75” x .75” | 0.50625 | .3V
ACT-0750-020 | ACT-0750 | 20 | .75” x .75” | 0.50625 | .3V
ACT-0750-005 | ACT-0750 | 5 | .75” x .75” | 0.50625 | .3V
ACT-0750-250 Opt C0.6 | ACT-0750 | 250 | .75” x .75” | 0.50625 | .3V
ACT-0750-200 Opt C0.6 | ACT-0750 | 200 | .75” x .75” | 0.50625 | .3V
ACT-0750-150 Opt C0.6 | ACT-0750 | 150 | .75” x .75” | 0.50625 | .3V
ACT-0750-100 Opt C0.6 | ACT-0750 | 100 | .75” x .75” | 0.50625 | .3V
ACT-0750-070 Opt C0.6 | ACT-0750 | 100 | .75” x .75” | 0.50625 | .3V
ACT-0750-050 Opt C0.6 | ACT-0750 | 50 | .75” x .75” | 0.50625 | .3V
ACT-0750-030 Opt C0.6 | ACT-0750 | 50 | .75” x .75” | 0.50625 | .3V

## Wire Size Chart (hidden)
Wire Size | Wire Diameter (inches) | Wire Size | Wire Diameter (inches) | Current (Amps)
18 AWG | 0.11 | 2000 MCM / kCMIL | 1.92 | 1200
16 AWG | 0.12 | 1750 MCM / kCMIL | 1.82 | 1000
14 AWG | 0.13 | 1500 MCM / kCMIL | 1.7 | 900
12 AWG | 0.15 | 1250 MCM / kCMIL | 1.58 | 800
10 AWG | 0.17 | 1000 MCM / kCMIL | 1.4 | 750
8 AWG | 0.24 | 900 MCM / kCMIL | 1.34 | 650
6 AWG | 0.32 | 800 MCM / kCMIL | 1.28 | 580
4 AWG | 0.37 | 750 MCM / kCMIL | 1.25 | 535
3 AWG | 0.4 | 700 MCM / kCMIL | 1.21 | 505
2 AWG | 0.43 | 600 MCM / kCMIL | 1.14 | 475
1 AWG | 0.51 | 500 MCM / kCMIL | 1.03 | 430
1/0' | 0.55 | 400 MCM / kCMIL | 0.94 | 380
2/0' | 0.59 | 350 MCM / kCMIL | 0.89 | 350
3/0' | 0.65 | 300 MCM / kCMIL | 0.84 | 320
4/0' | 0.7 | 250 MCM / kCMIL | 0.79 | 290
250 MCM / kCMIL | 0.79 | 4/0' | 0.7 | 260
300 MCM / kCMIL | 0.84 | 3/0' | 0.65 | 225
350 MCM / kCMIL | 0.89 | 2/0' | 0.59 | 200
400 MCM / kCMIL | 0.94 | 1/0' | 0.55 | 170
500 MCM / kCMIL | 1.03 | 1 AWG | 0.51 | 150
600 MCM / kCMIL | 1.14 | 2 AWG | 0.43 | 130
700 MCM / kCMIL | 1.21 | 3 AWG | 0.4 | 110
750 MCM / kCMIL | 1.25 | 4 AWG | 0.37 | 100
800 MCM / kCMIL | 1.28 | 6 AWG | 0.32 | 70
900 MCM / kCMIL | 1.34 | 8 AWG | 0.24 | 50
1000 MCM / kCMIL | 1.4 | 10 AWG | 0.17 | 30
1250 MCM / kCMIL | 1.58 | 12 AWG | 0.15 | 20
1500 MCM / kCMIL | 1.7 | 14 AWG | 0.13 | 15
1750 MCM / kCMIL | 1.82 | 16 AWG | 0.12 | 8
2000 MCM / kCMIL | 1.92 | 18 AWG | 0.11 | 5
Note on A1: Brian: NMC = kCMIL
Note on D1: Brian: NMC = kCMIL

## Voltage Loopup Table (hidden)
Voltage / Phase | Divider | Voltage | Power Factor
600/347 - 3 | 1039.2 | 600 | 1
480/277 - 3 | 831.36 | 480 | 1
415/240 - 3 | 718.78 | 415 | 1
400/230 - 3 | 692.8 | 400 | 1
240/120 - 1 | 415.68 | 240 | 1
208/120 - 3 | 360.256 | 208 | 1
208/120 - 1 | 208 | 208 | 1